**Part 3 – Enclosure Self Framing Design**

**General**

The buildings covered by these specifications will be of self-framing design, utilizing the roof and wall panels as the primary structural supporting members.

All buildings will be manufactured by Parkline, Inc., Winfield, WV or equal.

Each building will be supplied complete with all necessary component parts, including drill-in foundation anchors, to form a complete building system. All parts will be new and free from any defects or imperfections.

The building width and length will be measured from the outside of the building wall panels, and the height of the building will be the distance measured from the bottom surface of the base channel to the exterior juncture of the roof and side wall panels.

The building supplier will supply a complete set of building erection drawings showing the step-by-step construction instructions for the assembly of the building. The erection drawings will be prepared specifically for the building covered by these specifications showing the exact location of all roof and wall accessories and the exact anchor bolt locations required for each accessory.

**Building Specifications**

**Drawings and Design Data**

All buildings will be designed in accordance with the applicable sections of the latest edition of the AISC “Specifications for Structural Steel Buildings” and the AISI “Specifications for the Design of Cold-Formed Steel Structural Members”.

Each building will be designed for the following loads, in addition to the stationary weight (dead load) of the building. Reduction of gravity loads due to tributary loaded areas will not be permitted.

1. The vertical Live Load of the building will not be less than (\*) pounds per square foot applied

on the Horizontal projection of the roof. \*Per customer request but not less than 20psf or as

required by local code, whichever is greater.

2. The Ground Snow Load of the building will not be less than (\*) pounds per square foot. The

factored roof snow load will be applied on the Horizontal projection of the roof. \*Per

customer request or as required by local code, whichever is greater.

3. The design Wind Load of the building will not be less than (\*) miles per hour (3 second gust)

and will be distributed and applied in accordance with the applicable edition of the

“International Building Code” published by the International Code Council. \*Per customer

request or as required by local code, whichever is greater.

4. The design Seismic Load of the building will be calculated, distributed and applied in accordance with the applicable edition of the “International Building Code” published by the

International Code Council. A 0.2 second Spectral Response Acceleration of (\*) percent and

a 1.0 second Spectral Response Acceleration of (\*) percent will be used for design. \*Per

customer request or as required by local code, whichever is greater.

All combining and distributing of auxiliary equipment loads imposed on the building system will be done in accordance with the applicable edition of the “International Building Code” published by the International Code Council.

NOTE: The building designer is responsible for advising the building supplier of any auxiliary loads intended to be imposed on any building covered by these specifications.

Upon request, the selected building manufacturer will provide the building purchaser with a complete design certification signed and sealed by a registered professional engineer.

Parkline, Inc. designs all standard buildings using the applicable edition of the “International Building Code” (IBC) published by the International Code Council. Please note that many areas of the country require the use of state or local building codes which may be different from the “IBC”. Building codes can be markedly different from one another and are often revised at the local level. Therefore, it is the responsibility of the specifier to notify Parkline, Inc. of any building code(s) in effect for any particular building or provide Parkline, Inc. with contact information for the building inspector with jurisdiction over the building site.

**Roof and Exterior Wall Panels**

**Roof Panel Design**

Roof panels will be supplied in a single continuous length from eave line to ridge line on Gable buildings and from eave line to eave line on other buildings, and will be designed to tightly interlock so that no fasteners are required at intermediate points along the panel side laps.

Roof panels will be a maximum of 16” wide with a smooth surface between the interlocking side ribs. The interlocking ribs will be a minimum 3” high and will be turned upward. All roof panels will be factory punched for connection at the eave line of the building. There will be no fastener penetrations through the roof covering except at eave lines, ridge lines and roof accessory openings, such as skylights and ventilators.

**Roof Panel Finish (Standard)**

Roof panels shall be nominal 24-gauge steel coated on both sides with a coating of corrosion resistant aluminum-zinc alloy conforming to ASTM A 792 specification with the coating conforming to AZ55 standard by a continuous hot dipping process. Coating weight will be a minimum of 0.55 oz. of aluminum-zinc alloy per square foot of coated sheet equivalent to about 0.8 mil. thickness on each side. Minimum yield strength of panel material will be 50,000 PSI.

**Roof Panel Finish (Optional)**

Roof panels shall be nominal 24-gauge galvanized steel conforming to ASTM A 653 specifications with the galvanized coating conforming to G90 (0.90 oz. commercial) standards. Minimum yield strength of the panel material will be 50,000 PSI. All exterior surfaces of the galvanized steel roof panels will receive two factory, roller applied paint coats having a combined coating thickness of 0.8 to 1.1 mils of dry film thickness. The finished coat for the roof panels will be a white siliconized polyester formulation.

The roof panel color coating will carry a low fire hazard rating equal to a Class 1 material as defined by Factory Mutual. The panel coating will have achieved a Flame Spread Index of 0 and a Fuel Contributed Index of 5 or less when tested in accordance with ASTM E 84 test procedures.

The finish coat will be a white siliconized polyester formulation that will meet the following performance standards after 10 years continuous exposure in “normal” atmospheric conditions not containing corrosive fumes, such as chemicals or salt spray.

1. Panels will show no evidence of blistering, peeling or chipping.

2. Panels will not show surface chalking in excess of the No. 6 rating per ASTM D 4214,

Method A, as established by the American Society of Testing Materials (ASTM).

3. Panels will not show color change in excess of 7 Hunter units when measured in

accordance with the ASTM D 2244 standard after cleaning per ASTM D 3964.

The above performance standards will not apply where panels have been damaged by fire, radiation or other physical damage.

**Wall Panel Design**

Exterior wall panels of the building will be a single continuous length from the base channel to the roof line of the building at the side walls and end walls of the building except where interrupted by wall openings.

Wall panels will be 16” wide with a 3” deep inward-turned interlocking side rib. Wall panels will contain two 3/4” deep by 3-1/8” wide fluted recesses, each starting 2-7/16” from the panel edge.

Wall panels will be fastened internally to the base channel and eave cap of the building with 3/8” diameter plated machine bolts placed within the panel interlock. The fastening system will be designed so that no wall fasteners are exposed on the exterior surface of the walls.

Wall panels shall be nominal 24-gauge galvanized steel conforming to ASTM A 653 specifications with the galvanized coating conforming to G90 (0.90 oz. commercial) standards.

Minimum yield strength of the panel material will be 40,000 PSI. Panel material will be embossed with a random pattern pebble embosser of approximately 0.007-0.008 depth.

**Wall Panel Finish**

All exterior surfaces of the galvanized steel wall covering and exterior trim will receive a factory, roller applied paint coating having an exterior coating thickness of 0.95 to 1.1 mils of dry film thickness. The finish coat for wall panels will be a siliconized polyester formulation of one of the following Parkline colors:

Artic White, Desert Tan, Harvest Gold, Laurel Green, Roman Bronze, Shell Gray, Twilight Blue

Parkline’s standard roof is provided with a zinc and aluminum alloy coating, and Arctic White is available at an additional cost.

The wall panel color coating will carry a low fire hazard rating equal to a Class 1 material as defined by Factory Mutual. The panel coating will have achieved a Flame Spread Index of 0 and a Fuel Contributed Index of 5 or less when tested in accordance with ASTM E 84 test procedures.

Exterior color coatings will meet the following performance standards after 10 years continuous exposure in normal atmospheric conditions not containing corrosive fumes, such as chemical fumes or salt spray.

A. Panels will show no evidence of blistering, peeling or chipping. Paint finish will not peel, flake or otherwise lose adhesion to an extent that is apparent on ordinary visual observation. NOTE: Slight crazing or cracking may occur on roll-formed edges or break bends at the time of forming.

B. Panels will not show surface chalking in excess of the No. 8 rating per ASTM D 4214, Method A as established by the American Society of Testing Materials (ASTM).

C. Panels will not show color change in excess of five Hunter units when measured in accordance with the ASTM D 2244 standard after cleaning per ASTM D 3964.

The above performance standards will not apply where panels have been damaged by fire, radiation or other physical damage.

**Type ‘S’ (Single Slope)**

**Building widths: 5’-4” to 20’-0” wide in 16” increments**

**Roof Design**

Each ‘Type S’ building roof will be pitched: 5’-4” to 16’ wide buildings will have a 1-1/2” pitch over the building width and buildings greater than 16’ wide will have a 3” pitch. Roof panels will be interlocking and be attached to the wall cap through factory punched holes with #14 corrosion resistant fasteners.

The roof system will include a gutter and downspout system at the low side wall and matching rake trim at the building end walls. All gutters and trim will be nominal 26-gauge galvanized steel prepainted Arctic White or Roman Bronze.

**Wall Design**

The wall system will provide structural support for the roof and lateral support for the building. No secondary girt system will be required for structural support of the building wall system.

**Structural Framing**

Transmission of horizontal wind loads across the building will be made through the panel roof system and no separate roof or wall diagonal bracing will be required. Parkline ‘Type S’ buildings are self-supporting structures and will not depend on existing structures for support.

Where required for proper transmission of lateral wind loads, structural frame wind bents will be installed. Wind bents will consist of a bolted column and rafter assembly of steel conforming to ASTM A 36 specifications.

**Type ‘LT’ (Lean-To)**

**Building widths: 5’-4” to 20’-0” wide in 16” increments**

**Roof Design**

Each ‘Type LT’ building roof will be pitched: 5’-4” to 16’ wide buildings will have a 1-1/2” pitch over the building width and buildings greater than 16’ wide will have a 3” pitch. Roof panels will be interlocking and be attached to the wall cap through factory punched holes with #14 corrosion resistant fasteners.

The roof system will include a gutter and downspout system at the low side wall and matching rake trim at the building end walls. All gutters and trim will be nominal 26-gauge galvanized steel prepainted Arctic White or Roman Bronze.

**Wall Design**

The wall system will provide structural support for the roof and lateral support for the building. No secondary girt system will be required for structural support of the building wall system

**Structural Framing**

Transmission of horizontal wind loads across the building will be made through the panel roof system and no separate roof or wall diagonal bracing will be required. Parkline ‘Lean-To’ buildings are self-supporting structures and will not depend on existing structures for support.

Structural support and attachment of roof at existing building will be the responsibility of others. In snow prone areas, drifting should be considered.

**Type ‘AL’ (Gable)**

**Building widths: 8’-0” to 32’-0” wide in 4’-0” increments**

**Roof Design**

Each ‘Type AL’ building will have a center gable roof with a slope of 2” in 12” (8’-0” to 28’-0” wide) or 4” in 12” (32’-0” wide). The interlocking roof panels will vary in width up to 16” wide and in thickness from 0.024” thick to 0.044” thick depending upon the loading conditions. They will be fastened to an eave cap with 1/4” diameter 300 Series stainless steel bolts through factory punched holes. The ridge of the roof will be a welded double channel assembly sealed with a nominal 20-gauge steel ridge cover matching the roof in color. The interlocking panel roof system shall extend a minimum of 6” over the side wall panels and a minimum of 8” over the end wall panels of the building, except that buildings with 12” wide roof panels will have no end wall overhang.

The gable ends will be trimmed with nominal 26-gauge factory painted rake trim having matching ridge and eave cornices. Color will be Arctic White or Roman Bronze.

OPTIONAL: The eaves of the building will have nominal 26-gauge gutter and 2” x 3” downspouts factory painted to match the building’s rake trim. The system will be complete with all required outlet drops, elbows and connecting hardware.

**Wall Design**

The wall system will provide structural support for the roof and lateral support for the building. No secondary girt system will be required for structural support of the building wall system

**Structural Framing**

Strap and/or channel bracing components will be placed across the building width to allow transmission of horizontal wind loads. All wind bracing components will be not less than nominal 14-gauge galvanized steel.

Where required for proper transmission of lateral wind loads, structural frame windbents will be installed. Windbents will consist of a prime painted column and rafter bolted assembly of steel conforming to ASTM A 36 specifications

**Factory Assembled Building**

**Building Design**

Factory-assembled buildings consist of a self-framing building, using the walls and roof as the structural supporting system. Buildings can be supplied in single slope or gable roof design and may be shipped in multiple sections. The roof system will include gutter and rake trim for a finished appearance. Building to include accessories, steel base system, electrical, HVAC and interior finishes as required by the customer. All assemblies will be completed in a controlled environment to ensure a quality product. Where required, buildings will be shipped with necessary third-party inspection certificates and/or state labels. Off-loading, setting, and connection of utilities is not the responsibility of the building manufacturer

**Base Design**

Each building will be factory erected in a controlled environment on one of the following:

**Tube Skid**

A tube skid is to be used if the building is to be set on a customer-supplied concrete foundation.

**Angle Skid**

An angle skid is to be used if the building is to be set on a customer-supplied I-beam base, C-channel skid, or concrete foundation.

**Structural Skid w/ Floor**

A structural perimeter frame with floor system designed for (\*) psf live load is to be used if the building is to be set on a customer-supplied concrete foundation or piers. \*Per customer request but not less than 50 or as required by local code (based on building occupancy), whichever is greater.

**Factory Assembled Building**

**Lifting Design**

All factory assembled buildings will be designed for either a base lift or roof lift. Rigging required for lifting of the building will be provided by others

**Electrical Equipment**

Electrical equipment provided in building will be based on customer-supplied specifications. All electrical equipment to be installed per national electrical code

**HVAC**

Buildings that require heating and cooling will be equipped with an HVAC unit designed to meet the requirements given by the customer. HVAC system design will be required to meet the minimum national energy code. Heat loads generated from customer-supplied equipment inside building must be given to building supplier in order to size unit accurately

**Hollow Metal Doors**

**Door Leaf**

Door leaves will be 1-3/4” thick flush construction of a nominal 20-gauge galvanized steel, reinforced by lamination to a small cell honeycomb core. Leaves will be manufactured in accordance with ANSI/SDI-100, Grade 1, Model 1. (STC rating - 30, and U value - .14).

**Door Frame**

Door frames will be either 3” deep, single rabbit or 4-3/4” deep, double rabbeted type, of nominal 16-gauge galvanized steel. Frames will have hinge reinforcement of a nominal 7-gauge and lock reinforcement of a nominal 16-gauge.

**Door Assembly**

All doors will be provided “assembled” in their frames with all hardware, except door levers, knobs, bars or closers installed on door leaf. (Double swing doors will require some field assembly).

**Door Finish (Standard)**

All leaves and frames will be factory painted with one coat of baked on primer

**Door Finish (Optional)**

Door leaf and frame will receive one factory applied finish coat of polyester paint to match the wall color

**Hollow Metal Doors**

**Door Hardware (Standard)**

A. (3) 4-1/2” x 4-1/2” hinges per ANSI #A5133-630 satin stainless steel finish with non-rising pins.

B. 3-11/16” wide x 5/8” high extruded aluminum threshold.

C. 11/16” x 1/4” aluminum/vinyl weatherstripping.

D. Mortise lock set per ANSI A 156.13, Series 1000, Grade 1, Function F13, 626 satin chrome finish (levers both sides).

**Door Hardware (Optional)**

A. Cylindrical key in lever lock set per ANSI A 156.2, Series 4000, Grade 2, Function F81, 626 satin chrome finish.

B. Rim type “push pad” panic device per ANSI A 156.3, Type 1 Grade 2, Function 08, 689 aluminum lacquer finish interior, 626 satin chrome finish exterior.

C. Passage set per ANSI A 156.2, Series 4000, Grade 2, Function F75, 626 satin stainless steel

finish.

D. Door closer is certified to conform to ANSI 156.4, Grade 1 and meets entrance accessibility

requirements with 689 aluminum lacquer finish.

E. 23” wide x 20” high adjustable blade louver with mesh insect screen. Free area of approximately 155 square inches.

F. ADA (The Americans With Disabilities Act) Package.

G. Insulated leaf, foamed-in-place polyurethane core, bonded to 18-gauge galvanized steel face

sheets, having a .087 U value and STC rating of 26.

H. (3) 4-1/2” x 4-1/2” standard weight ball bearing hinges per ANSI A 5112, 630 satin stainless finish with non-rising pins.

**Framed Openings**

**Framed Openings for Overhead Doors**

Framed openings for overhead doors will be constructed from nominal 12-gauge galvanized steel. The 8” wide jambs will be provided with a minimum 2-1/2” wide inside surface for field mounting of overhead door track and hardware. Head and jambs will be provided with nominal 24-gauge covers, embossed, painted wall color.

**Removable Wall Sections**

A removable wall section will consist of a framed opening capable of supporting roof and wall loads when the wall section is removed. The removable wall section will consist of the same materials as the permanent wall. Section will be removable by unbolting from inside the building.

**Wall Opening Kit**

All necessary framing and connectors to structurally replace the panels removed by wall opening. All trim and flashings required to make a unit placed in the opening weathertight will be provided by the supplier of the unit being installed. Standard Widths: 1’-4”, 2’-8”, 4’-0”, 5’-4”, 6’-8” (heights as required)

**Windows**

**Horizontal Sliding Windows**

Sliding windows will be furnished factory-glazed and complete with all attaching hardware and screen. The window unit will be factory-assembled for single unit installation. All window sash sections will be of 0.05” minimum extruded aluminum and will be color finished in white or bronze baked enamel. All windows, unless otherwise noted, will be factory glazed with 5/8” minimum insulated glass.

**Fixed Windows**

Fixed windows will be furnished factory-glazed and complete with all attaching hardware. The window unit will be factory-assembled for single unit installation. All window sash sections will be formed from nominal 18-gauge galvanized G90 steel and factory color finished white or bronze baked on enamel.

**Wall Louvers**

**Adjustable Wall Louvers**

Adjustable louvers will be of self-framing design. The louver frame will be of nominal 14-gauge formed aluminum and the louver blades will be nominal 12-gauge extruded aluminum. Finish will be natural mill finish and will not require field painting. Blades will be pivoted on 1/2” diameter aluminum pivot pins through nylon flanged bearings and operated by means of a pull-bar operating handle. All louvers will be complete with an exterior mounted 18-14 aluminum mesh insect screen.

**Gable Louver**

Gable louvers will be fixed blade type with blades set on a 45 degree slope. Blades and frames will be 14-gauge extruded aluminum with natural mill finish. Louvers will include 18-14 aluminum mesh insect screens.

NOTE: Gable louvers are not available for 8’-0” wide buildings

**Fixed Louver**

Fixed louvers will be aluminum, general purpose type of self-framing design with free area of 63 sq. inches. Finish will be an aluminum mill finish. All louvers will be complete with #8 mesh screen.

NOTE: Designer must specify louver sill height. Minimum sill or head height is 6”.

**Roof Vents**

**Circular Roof Ventilator**

Stationary ventilator for 3” or 4” roof will be gravity type with standard 12” diameter throat, fabricated from aluminum, and will be furnished complete with bird screen, operable disc type damper with chain, and base.

NOTE: Not available for 6” roof.

**Power Roof Exhauster**

Aluminum power roof exhauster for 3” or 4” roof will have a 12” diameter throat, capable of 280 CFM air movement at 1/8” static pressure and will be equipped with U.L. listed adjustable thermostat. Power requirements of exhauster will be .86 amps at 115 volts. An intake louver of 115 square inches minimum free air area will be required for each exhauster.

NOTE: Not available for 6” roof.

**Turbine Vent**

Turbine vent will be wind-driven rotary type gravity roof ventilator, with 8” or 12” diameter throat, fabricated from galvanized steel, externally braced

**Exterior Roof Options**

**Ridge Ventilator (Gable Buildings only)**

Ridge ventilator will be of gravity type with 4” throat and chain operated vertical lift dampers. Ventilators will be made of nominal 24-gauge steel, factory-painted white on all visible exterior galvanized surfaces. Top of the ventilator will have a bird screen cover

**Roof Curb**

Roof curbs will be constructed of minimum 18-gauge Galvalume steel. Minimum height of curb will be 5”, but not less than 1” above adjoining roof panel ribs. All flashings will be provided to ensure water tightness. All roof curb support members are constructed of minimum 14-gauge galvanized steel. Optional hatch or cover is available.

Standard sizes:

2’-8” x 2’-8” (2’-5” x 2’-5” Inside Dimensions)

4’-0” x 4’-0” (3’-9” x 3’-9” Inside Dimensions)

NOTE: Single slope building sections shown. Interior clear height may be affected

**Skylights**

A skylight panel will be a flat polycarbonate sheet, factory-assembled into a standard 16” wide flush interlocking panel. The polycarbonate sheet will be 1/8” thick, clear with a matte finish, having a light transmission factor of approximately 70%. The panel will meet ANSI Z 97.1 safety glazing standards and UL 94 flammability rating.

NOTE: 1. Skylight panels are field located as required.

2. Skylight panels must have a minimum of one solid panel between each skylight for proper roof support.

3. Skylights for 6” rib roof panels are 8” wide in lieu of 12”.

**Vertical Facade**

The fascia system will consist of nominal 18-gauge galvanized steel framing and nominal 24-gauge embossed facing panels. Fascia will be attached to the upstanding legs of the interlocking roof panels with no penetration of the roof surface. The embossed fascia panels are available in flush or fluted profile. Buildings with fascias in heavy snow areas should allow 10 psf additional live load for snow buildup. Fascias are not recommended for 40 psf snow load areas.

NOTE: Flush fascia panels are available in bronze or white. Fluted fascia panels are available in seven standard colors.

**Interior Finishes**

**Formed Wall Liner**

Interior liner panels will have a maximum coverage width of 32” and overlap with the adjoining liner panel. The interior surface will have 1/4” high x 1” wide ribs on 8” centers. The liner will be continuous length from base to eave, except where interrupted by wall accessories. The exterior panel void will have a 16” wide, 3-1/2” thick unfaced R13 fiberglass insulation.

NOTE: Buildings that are heated and/or cooled must meet the requirements of the International Energy Conservative Code in effect for the building’s final destination. If you select an insulation system that does not meet these minimum requirements, we will add insulation to meet the code when the building is quoted.

**Optional**

A one inch wide thermal tape can be applied to the inside of the exterior panel ribs to abate thermal bridging between the joints.

A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.75, U-0.13) may be installed outside of the exterior panel ribs

A29 Acoustical Wall System will be accomplished by the system described above including thermal tape, except the liner panel will have 1/8” diameter perforations spaced on 3/8” staggered centers. The system will have an NRC rating of 0.90 and STC rating of 29.

**Interior Finishes (Wall)**

**Roll-In Insulation**

The interior of the building will be insulated with 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation with separate white metalized polypropylene scrimkraft (PSK) facing stretched across the interlocking panel ribs and held in place with a PVC 1-1/2” wide batten strip attached with #12 self-drilling fasteners.

Optional: A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.75, U-0.13) may be installed inside of the exterior panel ribs.

**Acoustical Wall System**

A48 Acoustical Wall System consists of a nominal 24-gauge fluted exterior panel with a minimum 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation in panel void. A 1/2” thick sound buffer board will separate the exterior wall system and a nominal 26-gauge flush metal septum panel. The septum panels will be installed perpendicular to the exterior wall panels with void filled with a minimum 16” wide, 3” thick R13 4# density fiberous acoustical insulation. A vibration retardant tape will be installed between the septum panel ribs and a perforated formed liner panel. The system will have an NRC of 1.00 and STC of 48. Wall accessories may affect overall performance. For panel profile, please see FORMED WALL LINER above. This system has NOT been sound tested.

NOTE: Buildings that are heated and/or cooled must meet the requirements of the International Energy Conservation Code in effect for the building’s final destination. If you select an insulation system that does not meet these minimum requirements, we will add insulation to meet the code when the building is quoted

**Lock-In Wall Liner**

The interior of the building will be finished with a factory-assembled insulated metal liner panel having no exposed fasteners except at the matching base, ceiling and accessory trim. Liner panels will be 16” wide, nominal 26-gauge, embossed, galvanized steel, prepainted Arctic White. Insulation will be non-combustible, nominal 1” thick, 2# minimum density fiberglass laminated to the liner panel.

**Optional**

The void between the exterior wall panel and the lock-in liner panel will be insulated with 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation

A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.75, U-0.13) may be installed inside of the exterior panel ribs

**Lock-In Plus Wall Liner**

The interior of the building will be finished with a factory-assembled, insulated metal liner panel having no exposed fasteners except at the matching base, ceiling and accessory trim. The liner system will have a concealed insulating board of 1-1/2” thick polyisocyanurate foam impaled on rib clips, and the void between the exterior wall panel and the lock-in liner panel will be insulated with 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation. Liner panels will be 16” wide, nominal 26-gauge, embossed galvanized steel, prepainted Arctic White. Insulation will be non-combustible, nominal 1” thick, 2# minimum density fiberglass laminated to the liner panel.

Optional: A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.75, U-0.13) may be installed inside of the exterior panel ribs

**6” Studwall**

The interior of the building will be finished with a factory-painted, galvanized steel liner panel having a maximum coverage of 32” and overlap with the adjoining liner panel. The interior surface will have 1/4” high x 1” wide ribs on 8” centers. The liner will be continuous in length from base trim to ceiling trim except where interrupted by wall accessories. The interior liner panels will be attached to 3” thick x 1” wide x 14-gauge steel studs spaced 16” on center and located at the midpoint of each exterior wall panel. The void between the studs will be filled with 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation. The exterior panel void will be filled with 16” wide, 3-1/2” thick R13 unfaced fiberglass insulation.

Optional: A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.75, U-0.13) may be installed inside of the exterior panel ribs.

**Partition**

Partitions will be constructed of 3” x 16” interlocking flush-type smooth or embossed surfaced panels in a nominal 24-gauge galvanized steel, factory-painted Arctic White. Partitions will be furnished complete with base channel, wall cap and all required fasteners. Partitions will accept all wall accessories such as walk doors, framed openings, louvers, wall opening kits and windows. In addition to wall accessories, partitions can be supplied with all interior liners and insulation for a complete field-assembled system.

Optional: Partitions can be supplied embossed in nominal 20-gauge and unembossed in nominal 18-gauge galvanized steel, factory-painted Arctic White

**Interior Finishes (Roof)**

**Ceiling**

The metal ceiling system will consist of 3” deep, 16” wide interlocking panels of nominal 24-gauge embossed galvanized steel, factory painted Arctic White. The ceiling system will be supported at its perimeter by concealed angles. The ceiling system will be furnished complete with all necessary connectors and fasteners.

**Option R-30**

The ceiling will be insulated with 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation laid in panel void. A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.55, U-0.13) will be laid on top of the ceiling panel ribs. A second layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top at right angles to the panel ribs. The “U” value through the finished ceiling will be a maximum of 0.04 BTU’s per square foot when calculated in accordance with the “Zone Method” contained in ASHRAE “Handbook of Fundamentals”, 1981 edition. Clear height = eave height - 6” (single slope type buildings), eave height - 9” (gable type buildings).

**Option R-38**

The ceiling will be insulated with 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation laid in panel void. A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.55, U-0.13) will be laid on top of the ceiling panel ribs. A second layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top at right angles to the panel ribs. A third layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top, parallel to the ceiling panel ribs. The “U” value through the finished ceiling will be a maximum of 0.032 BTU’s per square foot when calculated in accordance with the “Zone Method” contained in ASHRAE “Handbook of Fundamentals”, 1981 edition. Clear height = eave height - 8” (single slope type buildings), eave height - 11” (gable type buildings).

**Option R-49**

The ceiling will be insulated with 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation laid in panel void. A 1/4” layer of continuous, reflective, polyethylene insulation (R-7.55, U-0.13) will be laid on top of the ceiling panel ribs. A second layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top at right angles to the panel ribs. A third layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top, parallel to the ceiling panel ribs. A fourth layer of 16” wide by 3-1/2” thick R13 unfaced fiberglass insulation will be laid on top at right angles to the panel ribs. The “U” value through the finished ceiling will be a maximum of 0.025 BTU’s per square foot when calculated in accordance with the “Zone Method” contained in ASHRAE “Handbook of Fundamentals”, 1981 edition. Clear height = eave height - 11” (single slope type buildings), eave height - 13” (gable type buildings).

**Blanket Roof Insulation**

Roof insulations will consist of 48” wide, 3” thick, 6# density fiberglass faced on its exposed side with a white metalized polypropylene scrimkraft facing. The faced insulation material will have a UL Flame Spread Rating of 25 when tested in accordance with UL 723 ASTM E 84 procedures. Insulation will be supported at the roof line by means of mechanical clips spaced on maximum 4’-0” centers and will be sealed by means of 2” side tab on facing

**Therma-Roof**

The Therma-Roof insulation system will consist of two layers of 1-1/2” thick, 48” wide polyisocyanurate foam board faced with a white embossed foil on the exposed interior surface. The roof insulation system will include metal supporting tees on 4’ centers and all trim required for a finished interior appearance. No metal-to-metal contact between the insulation system and exterior roof or wall covering will be permitted. The insulation will have a maximum UL Flame Spread Rating of 25, Fuel Contributed Rating of 10 and Smoke Developed Rating of 155-190 when tested in accordance with UL 723 testing methods and will meet the requirements of the Underwriters Laboratories “Wall-Ceiling” Construction Classification.

NOTE: Insulation thickness will be 3”. (Two layers of 1-1/2” thermax board insulation)

End of Section