. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .. . . . . . . . . . . . . . . . . . . . . . . . . . . .  . . . . . . . . . . . . . . . .

VARIABLE SPEED DRIVE SIZING CHECKLIST

CHECK LIST

BGVSDSC

| JOB: |  |  |  |  |  |  | PART NUMBER: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CUSTOMER NAME: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CUSTOMER ADDRESS: |  |  |  |  |  |  | DATE: |  |  |  |  |  |  |
|  |  |  |  |  |  |  | APPLICATION: |  |  |  |  |  |  |
|  |  |  |  |  |  |  | PO #: |  |  |  |  |  |  |
| CONTACT NAME: |  |  |  |  |  |  | PREPARED BY: |  |  |  |  |  |  |
| STANDARD FEATURES / CAPABILITIES |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ENCLOSURE RATING |  | INDOOR |  |  |  |  |  | OUTDOOR |  |  |  |  |  |
|  IP20 CHASSIS |  |  TYPE 1 |  |  |  TYPE 12 |  |  |  TYPE 3R |  |  |  |  TYPE 4X |  |
| SYSTEM CONTROL |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  Differential Pressure |  |  Pressure |  |  |  Speed |  |  |  Level |  |  |  |  Flow |  |
| INPUT/OUTPUT OPTIONS - QUANTITY REQUIRED |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ANALOG INPUT |  | DIGITAL INPUT |  |  | ANALOG OUTPUT |  |  | DIGITAL OUTPUT |  |  |  | RELAY OUTPUT |  |
| BMS PROTOCOL |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  MODBUS RTU |  |  BACNET MSTP |  |  |  PROFIBUS |  |  |  DEVICENET |  |  |  |  OTHER |  |
|  NOT REQUIRED |  |  |  |  |  |  |  | Specify Protocol (OTHER): |  |  |  |  |  |
| SITE SPECIFIC DATA: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MEASURED LINE TO LINE VOLTAGE |  |  | *V (Average) |  |  |  | **V (IMBALANCE) % |  | MEASURED LINE TO GROUND VOLTAGE |  |  |  |  |
| L1 - L2 |  |  |  |  |  |  |  |  | L1 - Ground |  |  |  |  |
| L2 - L3 |  |  |  |  |  |  |  |  | L2 - Ground |  |  |  |  |
| L1 - L3 |  |  |  |  |  |  |  |  | L3 - Ground |  |  |  |  |
| VOLTAGE CALCULATIONS: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MOTOR INFORMATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SPECIFIED INPUT PHASE/VOLTAGE |  |  | NOMINAL MOTOR HP: |  |  |  |  |  |  |  |  |  |  |
| 1PH / 208 - 230 V |  |  |  < 0.75 |  |  | 7.5 |  |  |  | 40 |  |  |  |
| 3PH / 208 - 230 V |  |  | 1 |  |  | 10 |  |  |  | 50 |  |  |  |
| 1PH / 380 - 460 V |  |  | 1.5 |  |  | 15 |  |  |  | 60 |  |  |  |
| 3PH / 380 - 460 V |  |  | 2 |  |  | 20 |  |  |  | 75 |  |  |  |
| 3PH / 575 V |  |  | 3 |  |  | 25 |  |  |  | 100 |  |  |  |
| 1PH / 115 V |  |  | 5 |  |  | 30 |  |  |  | 125 |  |  |  |
| MOTOR AMPERAGE (SFA / FLA) |  | / |  |  |  |  |  | AMBIENT TEMPERATURE |  |  |  |  |  |
| LOAD WIRE LENGTH |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  < 50 Feet |  |  300 Feet Max. |  |  |  1000 Feet Max. |  |  |  ≤ 1500 Feet |  |  |  |  > 1500 Feet |  |
| MOTOR PROTECTION - Over 50 feet will require a reactor or filter to protect the motor. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  No Filter |  |  Load Reactor |  |  |  DV/DT Filter |  |  |  Sine Wave Filter |  |  |  |  |  |

For Bell & Gossett Controller Information: www.bellgossett.com                                                    CONTROLS TECHNICAL HOTLINE:  866-673-0445

| The type of transformer and the connection configuration feeding a drive plays an important role in its performance and safety. The following is a brief description of some of the more common configurations and a discussion of their virtues and shortcomings. Always ask what type of power system the site has before sizing the drive. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ELECTRICAL POWER SUPPLY VARIATIONS |  |  |  |  |  |
| Nominal Voltage | V Phase to Gnd |  |  | Type of Transformer | NOTES |
|  | L1 to Gnd | L2 to Gnd | L3 to Gnd |  |  |
| 208V | 120V |  |  | Wye | Most common. Provides rebalancing of unbalanced voltage with a 30° phase shift. |
| 480V | 277V |  |  |  |  |
| 575V | 332V |  |  |  |  |
| 240V | Various |  |  | Floating Delta | The phases have no true reference to ground |
| 480V |  |  |  |  |  |
| 575V |  |  |  |  |  |
| 240V | 0V | 240V | 240V | Corner Ground Delta | One phase connected to ground. Other 2 phases = line voltage |
| 480V | 0V | 480V | 480V |  |  |
| 240V | 208V | 120V | 120V | Delta with Wild Leg | One phase center tapped to derive a different voltage |
| 480V | 415V | 240V | 240V |  |  |
| ALL 3 PHASE | Look for 2 xformer cans on the power pole! |  |  | Open Delta | Generating 3 phase power from just 2 phases of a transformer |
| DRIVE MODIFICATIONS BASED UPON POWER SUPPLY |  |  |  |  |  |
| Wye | Aquavar SPD | Check Line to Ground voltages are within imbalance (3%). |  |  |  |
|  | Aquavar CPC | Install EMC filter screws EM1/EM3 or F1/F2 depending upon drive frame size. |  |  |  |
|  | Technologic & IPC | Check Line to Ground voltages are within imbalance (3%). |  |  |  |
| Floating Delta | Aquavar SPD | Follow procedure: Disconnecting EMC Filter and MOV's per IM213. |  |  |  |
|  | Aquavar CPC | Remove the line to ground EMC filter components by removing EM1 and EM3 or F1 and F2. Refer to “IT systems” in the table below. |  |  |  |
|  | Technologic & IPC | Set Parameter 14-50 RFI FILTER to [Off]. |  |  |  |
| Corner Grounded Delta | Aquavar SPD | Follow procedure: Disconnecting EMC Filter and MOV's per IM213. |  |  |  |
|  | Aquavar CPC | For R4 or N4 frame size, remove EM3. Leave EM1 connected. For R5/N5 and R6/N6 leave the screws in F1/F2 installed (Refer to the “Corner grounded TN systems” column in the table below). |  |  |  |
|  | Technologic & IPC | Set Parameter 14-50 RFI FILTER to [Off]. |  |  |  |
| Delta with Wild Leg | Aquavar SPD | Follow procedure: Disconnecting EMC Filter and MOV's per IM213. |  |  |  |
|  | Aquavar CPC | Refer to the “Corner grounded TN systems” column in the table below. |  |  |  |
|  | Technologic & IPC | Set Parameter 14-50 RFI FILTER to [Off]. |  |  |  |
| Open Delta | Aquavar SPD | Use a derated (oversized) three phase drive wired for single phase input supply. Drive output amperage to be derated by 50% to accommodate the single phase input. |  |  |  |
|  | Aquavar CPC |  |  |  |  |
|  | Technologic & IPC | Use dedicated single phase drive wired with the balanced input legs. |  |  |  |
| Table to be used for CPC ONLY | Frame Sizes | Screw | Symmetrically Grounded TN Systems (TN-S Systems) | Corner Grounded TN Systems | IT Systems (ungrounded or high-resistance grounded [> 30 ohm]) |
|  | R1…R3 | EM1 | x | x | • |
|  |  | EM31 | x | • | • |
|  | R4 | EM1 | x | x | — |
|  |  | EM31 | x | — | — |
|  | R5…R6 | F1 | x | x | — |
|  |  | F2 | x | x | — |
|  | x = Install the screw. (EMC filter will be connected) • = Replace the screw with the provided polyamide screw. (EMC filter will be connected) — = Remove the screw. (EMC filter will be connected) 1 = ACS550-U1 drives are shipped with screw EM3 already removed. |  |  |  |  |

Xylem Inc.

www.bellgossett.com

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

CentriPro and Aquavar are trademarks of Xylem Inc. or one of its subsidiaries.

© 2015 Xylem Inc.    BGVSDSC     January 2015                                                                                                                    CONTROLS TECHNICAL HOTLINE:  866-673-0445