

**SPECIFICATIONS** e-1531

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

DIVISION 15- MECHANICAL

Section 15540 - HVAC Pumps and Specialties

**1.00 PART 1 -GENERAL**

**1.01 DESCRIPTION OF WORK:**

A. Provide pumps and required system trim for heating, chilled water, and dual temperature water systems including all related appurtenances for a complete and operating systems.

**1.02 SECTION INCLUDES:**

1. End Suction, Close Coupled Pump (Foot Mounted)

**1.03 RELATED DOCUMENTS:**

1. Drawings and general provisions of the Contract, including General and supplementary Conditions and Division 1 Specification Sections, apply to these Sections.
	* Section \*\*\* - Alignment of Rotating Equipment
	* Section \*\*\* - Cast-in-Place Concrete
	* Section \*\*\* - Mechanical General Requirements
	* Section \*\*\* - Supports, Anchors, and Sleeves
	* Section \*\*\* - Motors and Starters
	* Section \*\*\* - Drives
	* Section \*\*\* - Mechanical Identification
	* Section \*\*\* - Vibration Isolation
	* Section \*\*\* - Piping Insulation
	* Section \*\*\* - Equipment Installation
	* Section \*\*\* - Hydronic Piping and Specialties
	* Section \*\*\* - Testing, Adjusting, and Balancing
	* Section \*\*\* - Meters and Gauges
	* Section \*\*\* - Electrical

**1.04 QUALITY ASSURANCE:**

1. All equipment or components of this specification section shall meet or exceed the requirements and quality of the items herein specified, or as denoted on the drawings.
2. Ensure pump operation at specified system fluid temperatures without vapor binding and cavitation, are non-overloading in parallel or individual operation, and operate to ANSI/HI 9.6.3.1 standard for Preferred Operating Region (POR) unless otherwise approved by the engineer. The pump NPSH shall confirm to the ANSI/HI 9.6.1-1997 standards for *Centrifugal and Vertical Pumps for NPSH Margin*.
3. Ensure pump pressure ratings are at least equal to system’s maximum operating pressure at point where installed, but not less than specified.
4. Equipment manufacturer shall be a company specializing in manufacture, assembly, and field performance of provided equipment with a minimum of 20 years experience.
5. Equipment provider shall be responsible for providing certified equipment start-up and, when noted, an in the field certified training session. New pump start-up shall be for the purpose of determining pump alignment, lubrication, voltage, and amperage readings. All proper electrical connections, pump’s balance, discharge and suction gauge readings, and adjustment of head, if required. A copy of the start-up report shall be made and sent to both the contractor and to the Engineer.

**1.05 PRODUCT HANDLING:**

A. Protection: Use all means necessary to protect equipment before, during, and after installation.

B. Replacement and Repair: All scratched, dented, and otherwise damaged units shall be repaired or replaced as directed by the Architect Engineer.

**1.06 REGULATORY REQUIREMENTS:**

1. Conform to Health/Life Safety Code for Public Schools
2. Conform to International Mechanical Code
3. Conform to BOCA National Building Code
4. Conform to BOCA National Fire Protection Code
5. Conform to State of Illinois Plumbing Code
6. Conform to National Electric Code NFPA 70
7. Conform to Illinois Accessibility Code
8. Conform to applicable ANSI/HI standards
9. Products: Listed and classified by Underwriters Laboratories, Inc. as suitable for the purpose specified and indicated.

**1.07 SUBMITTAL:**

A. Submit each item in this article according to the Conditions of the Contract and Division 1 Specification Sections.

1. Submit manufacturer’s installation instructions under provisions of General Conditions and Division 1.
2. Product Data including certified performance curves and rated capacities of selected models, weights (shipping, installed, and operating), furnished specialties, and accessories. Indicate pump’s operating point on curves.
3. Complete Package information Product Data including:
	* System summary sheet (where applicable)
	* Sequence of Operation
	* Shop drawing indicating dimensions, required clearances and location and size of each field connection
	* Power and control wiring diagram
	* System profile analysis including pump curves, system curve, and variable speed pump curves (where applicable)
	* Pump data sheets - Rated capacities of selected models and indication of pump’s operating point on curves.
	* Submittals on furnished specialties and accessories
	* Submittals must be specific to this project. Generic submittals will not be accepted
4. Hanging and support requirements should follow the recommendations in the manufacturer’s installation instructions.
5. A detailed weighted average pump efficiency-Part Load Efficiency Value (PLEV) - Pump Rating Report shall be submitted for each pump. Pump PLEV shall be based on the standard load profile developed in AHRI 550/590-1998 also known as IPLV or Integrated Part Load Value. The pump PLEV value shall be expressed with load weighting pump PLEV = 1 / (0.01/A+0.42/B+0.45/C+0.12/D) & shall be based points on A: 100%, B: 75%, C: 50% and D: 25%. Each Pump Efficiency ratings shall be shown with flow matched to load percentage and Specified Control Head. Actual job specific load profile weighting may be substituted for standard IPLV weighting.
6. Pump and motor must meet minimum Department of Energy requirements and have a PEICL value less than 1.

**1.08 OPERATION AND MAINTENANCE DATA:**

1. Submit Operation and Maintenance information under provisions of Division 15 "Mechanical General Requirements" and the provisions of the General Conditions and Division 1.

B. Operation and Maintenance Data: Include installation instructions, assembly views, lubrication instructions, and replacement parts lists.

C. Under provisions of commissioning documentation; testing of pumps, as well as training of owner’s operation and maintenance personnel may be required in cooperation with the commissioning consultant.

**1.09 DELIVERY, STORAGE, AND HANDLING:**

A. Deliver materials to the site in such a matter as to protect the materials from shipping and handling damage. Provide materials on factory provided shipping skids and lifting lugs if required for handling. Materials damaged by the elements should be packaged in such a matter that they could withstand short-term exposure to the elements during transportation.

B. Store materials in clean, dry place and protect from weather and construction traffic. Handle carefully to avoid damage.

**1.10 WARRANTY:**

A. Provide a minimum One (1) year warranty on materials and installation under provision of Section 15010.

**1.11 EXTRA MATERIALS:**

A. Provide one (1) set of mechanical seals for each model type of primary pump scheduled.

**2.00 PART 2- PRODUCTS**

1. The specifying engineer reserves the right to specify a primary supplier / lead spec manufacturer on all supplied schedule and specification documents. These primary suppliers have lead their respective industry in research and development and their products have had proven track records in the field. These primary suppliers, in the opinion of this engineering firm, produce a superior product to the alternately listed manufacturers. The contractor may choose to supply equivalent equipment as manufactured by the alternately specified manufacturer. This alternately specified equipment shall be supplied on a deduct alternate basis and based on the approval of the supplied alternate manufacturer’s submittals.

The use of a primary supplier and deduct alternates protects the specifying engineer’s design concept, but allows for a check-and-balance system to protect the post-commissioning owner.

**2.07 END SUCTION CLOSED COUPLED PUMPS (FOOT MOUNTED):**

A. Manufacturer:

1. Contractor shall furnish and install new end suction closed coupled pumps for chilled water and hot water heating systems as indicated on the drawings. Pumps shall be as manufactured by **Bell & Gossett** under base bid. Equivalent units as manufactured by others may be submitted as deduct alternates. Pumps shall meet types, sizes, capacities, and characteristics as scheduled on the Equipment Schedule drawings.

B. End Suction Closed Coupled Pump (Foot Mounted):

* 1. The pumps shall be close coupled, foot mounted, single stage, end suction, vertical split case design, in stainless steel fitted construction specifically designed for quiet operation. Suitable standard operations at 225 F and 175 PSIG working pressure. The pump internals shall be capable of being services without disturbing piping connections.
	2. The pumps shall have a solid SAE1144 steel shaft that is integral to the motor. A non-ferrous shaft sleeve shall be employed to completely cover the wetted area under the seal.
	3. The motor bearings shall support the shaft via heavy-duty grease lubricated ball bearings.
	4. Pump shall be equipped with an internally flushed mechanical seal assembly installed in an enlarged tapered seal chamber. Seal assembly shall have a brass housing, Buna bellows and seat gasket, stainless steel spring, and be of a carbon ceramic design with the carbon face rotating against a stationary ceramic face.
	5. Pump shaft shall connect to a stainless steel impeller. Impeller shall be hydraulically and dynamically balanced, keyed to the shaft and secured by a stainless steel locking cap screw or nut.
	6. Pump should be designed to allow for true back pull-out access to the pump’s working components for ease of maintenance.
	7. Pump volute shall be of a cast iron design for heating systems (or cast bronze for domestic water systems) with integrally cast pedestal volute support, rated for 175 PSIG with integral cast iron flanges drilled for 125# ANSI companion flanges. Volute shall include gauge ports at nozzles, and vent and drain ports.
	8. Motors shall meet scheduled horsepower, speed, voltage, and enclosure design. Motors shall have heavy-duty grease lubricated ball bearings to offset the additional bearing loads associated with the closed coupled pump design. Motors shall be non-overloading at any point on the pump curve and shall meet NEMA specifications.
	9. Pumps shall conform to ANSI/HI 9.6.3.1 standard for Preferred Operating Region (POR) unless otherwise approved by the engineer. The pump NPSH shall conform to the ANSI/HI 9.6.1-1997 standards for *Centrifugal and Vertical Pumps for NPSH Margin*.
	10. Pump shall be of a maintainable design and for ease of maintenance should use machine fit parts and not press fit components.
	11. Pump manufacturer shall be ISO-9001 certified.
	12. Each pump shall be factory tested and name-plated before shipment.
	13. Pump and motor must meet minimum Department of Energy requirements and have a PEICL value less than 1.

C. Accessories:

* 1. Where noted on schedule pumps shall be provided with all iron construction including: cast iron impeller, stainless steel shaft sleeve, and a stainless steel seal assembly housing.
	2. Where noted on schedule pumps shall be provided with internal bronze casing wear rings or modifications for special vertical mounting requirements.
	3. Where noted on schedule an EPT Tungsten/Carbide seal (250 F maximum operating temperature), FKM seal, or Teflon seal should be used in lieu of the Buna standard seal (225 F maximum operating temperature).
	4. Where noted on schedule a stuffing box designed may be used in lieu of the traditional internally flushed mechanical seal design. Pump shall be flushed single seal, flushed double seal, or packing gland type seal arrangements.
	5. Where noted on schedule pumping equipment may require one or all of the following tests: Certified Lab tests (unwitnessed), Hydraulic Institute Level B tests, or Witnessed Tests.
	6. Where noted on schedule a Bell & Gossett Sediment Separator shall be furnished for installation on the flushing line between the pump discharge flange and the seal area. The sediment separator is installed to increase the overall life expectancy of the seal, on inherently dirty systems. The separator shall remove dissolved solids from the flushing media before the fluid enters the seal area where it can damage and shorten the life of the seal.
	7. Where noted on schedule a Bell & Gossett Brazed Plate Heat Exchanger Kit shall be furnished for installation on the flushing line between the pump discharge flange and the seal area. The heat exchanger is installed to increase the overall life expectancy of the seal, on high temperature systems (greater than 225 F). The kit shall decrease the temperature of the flushing water being provided to the seal area as a flushing media to a temperature less than 225 F. Flushing temperatures higher than 225 F can damage and shorten the life of the seal.

**3.00 PART 3 - EXECUTION**

**3.01 INSTALLATION;**

1. All components shall be installed in accordance with manufacturer’s installation instructions.
2. Lubricate oil-lubricated pumps before start-up.
3. Pumps substitutions shall be provided with connection sizes equal to those scheduled. Pump connections shall not be downsized.
4. Pump substitutions shall not be provided at efficiencies less than those scheduled.
5. Reduction from line size to pump connection size shall be made with eccentric reducers attached to the pump with tops flat to allow continuity of flow.
6. Furnish and install triple duty valves on the discharge side of all pumps and furnish and install a line size shut-off valve on the suction side of all pumps. Anywhere that 5 straight pipe diameters of pipe can not be provided on the inlet side of a pump a suction diffuser shall be used to provide appropriate flow distribution into the eye of the pump’s impeller.
7. Provide temperature and pressure gauges where and as detailed or directed.
8. On systems where pump seals require flushing water or cooling water for a heat exchanger kit. Provide cooling water supply piping and connections and well as the return piping, if required. Piping should be of adequate size to pass required flow rate.
9. Proper access space around a device should be left for servicing the component. No less than the minimum recommended by the manufacturer.
10. Provide an adequate number of isolation valves for service and maintenance of the system and its components.
11. Circulating pump shall have sufficient capacity to circulate the scheduled GPM against the scheduled external head (feet) with the horsepower and speed as scheduled and/or as denoted on the drawings. Motors shall be of electrical characteristics as scheduled, denoted and/or as indicated on the electrical plans and specifications. Pump characteristics shall be such that the head of the pump under varying conditions shall not exceed the rated horsepower of the drive motor.
12. On systems where the final balancing procedure requires the triple duty valve to be throttled more than 25% to attain design flow (on a constant speed pumping system), and no future capacity has been built in to the pump the pump impeller must be trimmed to represent actual system head resistance. The pump provider and engineer of record, based on the balancing contractor’s reports, shall determine the final impeller trim diameter.
13. Mounting of vertical turbine pump motors (shipped loose) shall be the responsibility of the contractor. The motors shall be field mounted in accordance with manufacturer’s installation instructions.
14. Install foot mounted and base mounted pumps on vibration isolation pad or house keeping pad, via anchor bolts. Set and level and grout in place.
15. All piping shall be brought to equipment and pump connections in such a manner so as to prevent the possibility of any loads or stresses being applied to the connections or piping. All piping shall be fitted to the pumps even though piping adjustments may be required after the pipe is installed.
16. On components that require draining, contractor must provide piping to and discharging into appropriate drains.
17. Provide drains for bases and seals, piped to and discharging into floor drains.
18. Power wiring, as required, shall be the responsibility of the electrical contractor. All wiring shall be performed per manufacturers instruction and applicable state, federal, and local codes.
19. Control wiring for remote mounted switches and sensor / transmitters shall be the responsibility of the controls contractor. All wiring shall be performed per manufacturers instructions and applicable state, federal, and local codes.

**3.02 DEMONSTRATION;**

1. The system manufacturer or factory-trained representative shall provide start-up of the any packaged pumping system. This start-up shall include verification of proper installation, system initiation, adjustment and fine-tuning. Start-up shall not be considered complete until the sequence of operation, including alarms, has been sufficiently demonstrated to the owner or the owner’s designated representative. This jobsite visit shall occur only after all hook-ups, tie-ins, and terminations have been completed. A start-up reports outlining factory provided start-up and equipment performance shall be provided to the Architect/Engineer after it completion.
2. Manufacturer's trained representative shall provide on-site training for any packaged systems for the owner’s designated personnel. The training shall fully cover maintenance and operation of all system components.
3. Four (4) copies of the maintenance and operation manuals for all HVAC system components shall be submitted to the Architect/Engineer.
4. The system manufacturer must have complete HVAC training program available for owner’s personnel. The training sessions shall take place at the manufacturer’s facility and shall cover all aspects of HVAC system design, service, and operation.

END OF SECTION 15540



[www.bellgossett.com](http://www.bellgossett.com/)

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

© 2019 Xylem Inc. e-1531 Specifications