

**SPECIFICATIONS** Domestic Pump CS Duplex

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

**SECTION 232129**

AUTOMATIC CONDENSATE PUMP UNITS

**PART 1 GENERAL**

1.01 SECTION INCLUDES

# Unit shall be a Domestic® Pump automatic duplex condensate pumping unit, series CS™, as manufactured by Bell & Gossett, a Xylem brand®.

# Furnish and install extended life pumps with capacities as indicated in the plans.

1.02 RELATED SECTIONS

1. Section 232223.13 - Electric - driven steam condensate pumps
2. Section 262716 – Electrical cabinets and enclosures

1.03 REFERENCES

1. HI - Hydraulic Institute.
2. ANSI - American National Standards Institute.
3. NEMA - National Electrical Manufacturers Association.
4. UL - Underwriters Laboratories.
5. ETL - Electrical Testing Laboratories.
6. CSA - Canadian Standards Association.
7. NEC - National Electric Codes.
8. ISO - International Standards Organization.
9. IEC - International Electrotechnical Commission.

1.04 SUBMITTALS

1. Submit data cover sheet.
2. Unit description sheet.
3. Dimensional print(s).
4. Sales bulletin.
5. Piping diagram(s).
6. Wiring diagram(s).
7. Installation, operation & maintenance manual.

1.05 QUALITY ASSURANCE

1. The manufacturer shall have a minimum of 30 years experience in the design and construction of condensate return equipment.
2. The pump manufacturer shall be fully certified by the International Standards Organization per ISO 9001. Proof of this certification shall be furnished at the time of submittal.

# The manufacturer shall carry a minimum product liability insurance of $5,000,000.00 per occurrence.

# The unit shall be UL listed or recognized by Underwriters Laboratories, Inc. as a complete pumping package.

**PART 2 PRODUCTS**

2.01 MANUFACTURERS

# Subject to compliance with these specifications, the following manufacturers shall be acceptable:

1. Bell & Gossett, a Xylem brand Domestic series CS duplex.
2. Pre-approved equal.

2.02 COMPONENTS

## A. Condensate receiver

## The condensate receiver shall be of durable, Minimum 7 gauge steel thickness.

1. The receiver shall be a minimum of SA36 carbon steel or equivalent and feature an inlet, vent, and overflow opening to provide a means of secondary venting.
2. The receiver shall be furnished with two externally adjustable, NEMA 1, two-pole float switches for pump control.

# Water pump

**Items in parentheses denote optional items.**

# Two water pumps shall each be a series C35™ or C17™ bronze fitted, centrifugal pump, close-coupled to a 3500 RPM or 1750 RPM motor, permanently aligned, and flange mounted for vertical operation.

# Each pump shall include:

# One cast Iron volute with:

# One discharge gauge port tapping.

# One drain tapping.

# One dynamically balanced enclosed bronze centrifugal impeller.

# One renewable bronze wearing ring.

# One stainless steel shaft.

# Carbon/ceramic/stainless steel mechanical seal suitable for 250oF (121°C) operation.

# Each pump shall be sized for two times the system return rate.

# Each motor shall meet NEMA specifications and shall be the size, voltage, insulation class, duty rating and enclosure called for in the plans.

# Capacities and electrical characteristics for the pump shall be scheduled on the drawings.

1. (Water level gauge glass for visual tank level inspection.)
2. (Lifting eye bolts for unit placement.)
3. (A dial thermometer.)
4. (Pump discharge pressure gauge.)
5. (Two bronze fitted butterfly isolation valves (up to 115 GPM (435 L/M) pump capacity) between the pump suction and receiver for easy Isolation of the pump and motor assembly for servicing.)
6. (Cast iron inlet basket strainer with vertical self-cleaning bronze screen and large dirt pocket for sediment collection. The screen shall be easily removable for cleaning, requiring no additional floor space for servicing. This option ships loose for field installation.)
7. (A NEMA 1 automatic mechanical alternator to replace float switches. This option is also available in NEMA 4 as required.)
8. (TEFC motors as required.)
9. (Consolitrol® NEMA 2, UL electrical panel mounted and wired with drip lip and piano hinged door is available with the following options):
10. (NEMA 4 and NEMA 12 Electrical panels mounted and wired as required.)
11. (Two magnetic starters with thermal overload protection. Starters may be provided with disconnect devices, either:)
12. (Fusible disconnect with cover interlock or)
13. (Circuit breaker type with cover interlock.)
14. (One fused control circuit transformer when the motor voltage exceeds 250V.)
15. (Two selector switches.)
16. (“Off-Hand-Lead-Lag” selector switches)
17. (“Auto-Off-Hand” selector switches.)
18. (Two pump running pilot lights.)
19. (Two “Push to Test” buttons.)
20. (One numbered terminal strip.)
21. (Two auxiliary contacts on the magnetic starters normally open for remote monitoring of pump operation.)
22. (A removable control component mounting plate.)
23. (Two elapsed time meters (UL).)
24. (An audible alarm to indicate water level conditions.)
25. (Audible alarm is available with or without silencing relay.)
26. (A separate tank mounted level switch should be provided with audible alarm.)
27. (Alarm may be provided with alarm light to provide visual indication of alarm condition.)
28. (One single point power connection.)
29. (One electrical alternator.)
30. (Control power switching relay shall allow the switch over of control power from one pump to the other in the event of a power failure or pump failure.)
31. (Liquid tight conduit suitable for NEMA 2, NEMA 4 & NEMA 12 applications.)

**PART 3 EXECUTION**

* 1. INSTALLATION
1. Install equipment in accordance with manufacturer’s instructions.
2. Power wiring, as required, shall be the responsibility of the electrical contractor. All wiring shall be performed per manufacturer’s instructions and applicable state, federal and local codes.
3. All factory wiring shall be numbered for easy identification and the numbers shall coincide with those shown on the wiring diagram.
4. All interconnecting wiring between the pump controls and control panel shall be enclosed in liquid tight flexible conduit.
5. The unit shall be factory tested as a complete unit and the unit manufacturer shall furnish elementary and connection-wiring diagrams and piping diagrams. Installation and operation instructions shall also be provided.
6. The unit manufacturer shall furnish, mount on the unit and wire a NEMA 2 control cabinet with drip lip and piano hinged door.
7. The unit shall be shipped completely assembled.
8. The factory shall provide a certified test report.
9. Unit shall be a Domestic Pump Series CS duplex as manufactured by Bell & Gossett, Morton Grove, IL.

###### END OF SECTION



[www.bellgossett.com](http://www.bellgossett.com/)

Bell & Gossett is a trademark of Xylem Inc. or one of its subsidiaries.

© 2017 Xylem Inc. Domestic Pump CS Duplex Specifications